## Sheet1
Title | Goal | Year | Action space | Observation space | Reward | Algorithm | Training&Tools | Limitations, Future developments | Deployment | Link
Reinforcement Learning for Residential Heat Pump Operation | application of a RL approach to the operation of a residential district HP for space heating | 2024 (Germany) | Continuous 0kW - 100kW (HP power control) | endogenous: -SOC(t) (state of charge of heat storage) -loss(t) (heat losses of the heat storage) exogenous: -time -COP(Tamb) -el.price -D future demand -Tamb(t) | Rpos: keep the SOC in a specific range Rneg: penalizes in form of energy cost Rpos as a parabola with maximum reward at SOC=0.5 and minimum at 0.01 and 0.99 or asstep function Rneg = (−(D + lossh) · el.price) / Euro | PPO lr = from 0,001 to 0 during training nsteps = one year of data batch_size = 960steps (10 days) vectorized over 10 env |  |  |  | https://deliverypdf.ssrn.com/delivery.php?ID=130069006013118014118064119077004031002018053020030049097115004023002123078070083098115032065083096095023089104000118046108029094017099085082026119055084029051047102070115113025028092120050039014094014026015002107100101064113081029085022080073076107005086008127109030125004095008122106&EXT=pdf&INDEX=TRUE
An adaptive control framework based on Reinforcement learning to balance energy, comfort and hygiene in heat pump water heating systems | control HP to ensure a balance between energy consuption, hygiene (presence of bacteria) and comfort for water heating system | 2021 (Swiss) | Discrete heat pump ON-OFF | -Demand interval: divided in 5 liters interval (0-5, 5-10…) -Tamb -Tstorage (tank temperature) -Hours from overheat: hours from last heating above 60°C (hygiene purpose) -Time -Energy | energy reward = -a x Energy comfort reward = -b x max(40-Tstorage, 0) hygiene reward = -c x max(Hours from overheat-24, 0) a, b, c = 1, 2, 0.8 | DDQN |  |  |  | An adaptive control framework based on Reinforcement learning to balance energy, comfort and hygiene in heat pump water heating systems - IOPscience
Deep Reinforcement Learning for Building HVAC Control | HVAC control for minimizing building energy cost while maintaining comfortable temperature | 2017 (USA) | z different zone of temperature discrete levels of flow rate {f1, f2, f3, …, fm} action space=all possible combinations of flow rate n=mz | -current time(with releted data such as time-varying temperature requirements, electricity price, occupant activities) -zone temperature -environment disturbances(ambient temperature and solar irradiance intensity, forecast of weather data) | energy cost of the last control action - total penalty of temperature violation | DQN selfmade neural network 4 hidden layers activated by ReLU (50, 100, 200, 400 neurons) |  |  |  | Deep reinforcement learning for building HVAC control ¦ IEEE Conference Publication ¦ IEEE Xplore
Reinforcement Learning for Building Management Systems | how the performance of a chilled water system can be optimized using an actor-critic model | 2021 (USA) | continuous 0V-10V 0V: all the flow from the chillers 10V: all the flow from the thermal energy storage | -temperature that leaves the heat exchanger |  | actor-critic both implemented as fully connected neural network with no activation function |  |  |  | Reinforcement Learning for Building Management Systems (purdue.edu)
Practical Implementation and Evaluation of Deep Reinforcement Learning Control for a Radiant Heating System | Radiant heating control to improve thermal comfort and energy consumption | 2018 (Singapore China) | discrete system supply water temperature setpoint(°C) A={off,20,25,…,65} | the state is a stack of the current and n previous observations. each obs consists of: '-time(day, hour) -outdoor air temperature (◦C) -outdoor air relative humidity (%) -wind speed (m/s) -wind direction (degree from north) -diffuse solar radiation (W/m2) -direct solar radiation (W/m2) -HVAC system data Min-max normalization is used to normalize each item to 0-1. | Qmull = system heating demand since last step Occp = status flag (it indicates special hours of the day) β, τ = weights for heating demand and indoor thermal comfort ρ = scale factor to penalize PPD (Predicted Percentage of Dissatisfied) λ = penelaty level for indoor air temperature violation | A3C |  |  |  | (PDF) Practical Implementation and Evaluation of Deep Reinforcement Learning Control for a Radiant Heating System (researchgate.net)
Reinforcement Learning for Control of Building HVAC Systems | HVAC control to maintain temperature and humidity within the comfort limits and reduce energy usage | 2020 (USA) | continuous a = {Msa, Roa, Toa, Tsa} Msa = supply air flow rate Roa = outdoor air ratio Tca = conditioned air temperature Tsa = supply air temperature | -Tz = zone temperature -Wz = zone humidity -Toa = outdoor air temperature -Woa = outdoor air humidity -Ak-1 = previous control inputs | Denote by Xde the set of all desirable states: at time step k ≥ 0, Xk ∈ Xde, if the zone temperature and humidity are within desirable limits. Ek = energy consumed by fan, cooling coil and reheat coil Phigh > Plow are the penalties imposed for violating the comfort limits | Zap Q-learning Q-learning variant that converge quickly |  |  |  | https://ieeexplore.ieee.org/document/9147629
DeepComfort: Energy-Efficient Thermal Comfort Control in Buildings via Reinforcement Learning | Control setpoints and energy consumption of HVAC system | 2020 (Singapore China) | continuous control the setpoints of humidity and air temperature | indoor air temperature and humidity: Tin, Hin indoor air temperature and humidity: Tout, Hout thermal comfort prediction: -metabolic rate -clothing insulation -air temperature -mean radiance -air speed -humidity | Mt: predicted thermal comfort value [-3, 3] β: relative importance of energy consumption compared to the occupants' thermal comfort | DDPG tanh activation ADAM for gradient-based optimization learning rate: 0,001 discount factor: 0,001 batch size: 128 time slot: 30min episode: 48 time slots | Training performed offline TRNSYS to simulate the HVAC system and the thermal state in a building. 10000h of simulation data. Alghorithms implemented with PyTorch. The agent interact with TRNSYS with MySQL | using transfer learning to improve learning efficiency via the transfer of knowledge from different HVACs. Use model-based RL | simulation: building of 307m2 with 30 occupants and 40 computers. No real world test | https://ieeexplore.ieee.org/document/9085925
Deep Reinforcement Learning for Smart Home Energy Management | optimization of energy consumption and thermal comfort coordinating the ESS (energy storage system) and the HVAC system | 2020 (China) | continuous a ={ft, et} ft = [-dmax, cmax] d = ESS discharging power c = ESS charging power et = HVAC input power | -pt = renewable generation output -bt = nonshiftable power demand -Bt = ESS energy level -Tout = outdoor temperature -Tt = indoor temperature -vt = buying electricity price -t = time solt index in a day | C1 = energy consumption of HVAC C2 = ESS depreciation C3 = penalty for temperature deviation | DDPG two hidden layers in actor four hidden layers in critic | in simulations real-world traces extracted from Pecan Street database (data of a neighborhood in Austin) are used. No info about tools | More reasonable thermal comfort models and more types of controllable loads could be incorporated. | No real world test | https://ieeexplore.ieee.org/document/8919976
Comfort and energy management of multi-zone HVAC system based on Multi-Agent Deep Reinforcement Learning | save cost and maintain the indoor temperature comfort for multi-zone buildings. HVAC control temperature and humidity of N zone. | 2023 (China) | continuous air flow rate controlled by the fan control signal | -indoor temperature and humidity -outdoor temperature and humidity -Ot = zone occupancy at time slot t -λt = time-varying electricity price thermal comfort prediction: -metabolic rate -clothing insulation -air temperature -mean radiance -air speed -humidity | et = energy consumption pt = thermal comfort value | multi-agent TD3 | HVAC simulation environment using TRNSYS. Episode of one day with time slot of 15 minutes Algorithm implemented with PyTorch. Four zones of 256m2 with singapore weather. | better results than multi-agent DDPG | No real world test | https://ieeexplore.ieee.org/document/10241916